## Slide 1
FIELD TRAINING SERIES
Electrical Theory &
Energized-Line Safety
for Powerline Workers
A complete field-training program: theory → working hot → cover-up & tools → job planning & regulations
Lineworker Apprenticeship & Journeyman Refresher • Instructor Edition

## Slide 2
COURSE MAP
What This Course Covers
Six modules, building from first principles to the daily disciplines that keep crews alive.
■ Module 1 — Electrical theory: the science behind everything you touch
  – Atomic charge, voltage, current, resistance, power, AC vs DC, the grid
■ Module 2 — Electricity and the human body
  – Shock physiology, arc flash/blast, step & touch potential
■ Module 3 — Working around energized lines & equipment
  – Minimum approach distance, the second point of contact, isolation, cover-up, grounding
■ Module 4 — Tools of the trade
  – Rubber goods, live-line tools, grounds, testers, FR/arc-rated PPE — use, care, testing
■ Module 5 — Putting it to work in the field
  – Hazard assessment, the tailboard/job brief, roles, communication, rescue
■ Module 6 — Regulations & standards that govern the work
  – OSHA 1910.269 / 1926 Subpart V, NESC, ASTM/IEEE, recordkeeping
Course Overview
Powerline Electrical Theory & Safety | 02

## Slide 3
OBJECTIVES
Learning Objectives & How to Use This Training
By the end you will be able to
■ Explain voltage, current, resistance and power in plain terms
■ Describe how the grid moves power from plant to service
■ Identify what makes a circuit through the human body
■ Recognize and eliminate the second point of contact
■ Apply correct cover-up and minimum approach distances
■ Build an equipotential grounding zone
■ Lead a complete tailboard and hazard assessment
■ Cite the regulation behind each safe-work rule
How the material is structured
■ Theory first — you cannot work safely on what you don't understand
■ Each hazard is paired with its control
  – Recognize → isolate → protect → verify
■ DANGER / WARNING / BEST-PRACTICE call-outs flag the must-knows
■ Tables summarize numbers you will use on the job
■ Discuss every slide as a crew — this is a conversation, not a lecture
Course Overview
Powerline Electrical Theory & Safety | 03

## Slide 4
THE STAKES
Why This Training Exists
Line work is among the most hazardous trades in the country — and almost every incident traces back to a missed fundamental.
#1
Electrocution is a leading cause of lineworker fatalities
50 V
Can be enough to be lethal under the right conditions
0.1 s
A fault can evolve to an arc-flash in a fraction of a second
100%
Of electrical contacts are preventable with the right controls
These numbers are not here to scare you — they are here to remind you that the disciplines in this course are written in other workers' experience. Every rule has a reason. The goal of this training is simple: everyone goes home, every day.
Course Overview
Powerline Electrical Theory & Safety | 04

## Slide 5
MODULE
1
Electrical Theory Fundamentals
— What electricity actually is
— Voltage, current, resistance & power
— AC vs DC and three-phase systems
— Transformers and the grid
— Voltage classes you will encounter

## Slide 6
1.1 FIRST PRINCIPLES
What Is Electricity?
Before any rule makes sense, you have to know what is moving in the wire — and why it wants to get to ground.
■ All matter is built from atoms; atoms contain protons (+), neutrons (0) and electrons (–)
■ Electricity is the movement of electrons — specifically the flow of electric charge
  – In conductors, outer (“free”) electrons drift from atom to atom
  – That organized drift, driven by a difference in charge, is electric current
■ Two ways to talk about flow direction:
  – Conventional current: + to – (the convention used on prints and in formulas)
  – Electron flow: – to + (the physical reality)
■ Electricity always seeks to return to its source and will take every available path to ground
  – It does not “prefer” the easiest path — it uses ALL paths in proportion to their conductance
  – Your body can be one of those paths
Module 1 — Electrical Theory
Powerline Electrical Theory & Safety | 06

## Slide 7
1.2 MATERIALS
Conductors, Insulators & Semiconductors
Conductors (let electrons flow)
■ Copper, aluminum — line and busbar metals
■ Steel — structures, ground rods, messenger
■ Water with impurities, wet wood, the human body
  – Low resistance — current passes easily
■ Why we de-energize, isolate, and ground them
Insulators (resist electron flow)
■ Rubber, dry wood, glass, porcelain, fiberglass
■ Air — but only at sufficient distance (it can break down!)
■ EPDM rubber — the basis of our gloves & cover-up
  – High resistance — used to create separation
■ Semiconductors: silicon devices — reclosers, electronics, controls
Module 1 — Electrical Theory
Powerline Electrical Theory & Safety | 07

## Slide 8
1.3 VOLTAGE
Voltage — Electrical Pressure
■ Voltage (V) is the difference in electric potential between two points — the “pressure” that pushes current
■ Measured in volts; symbol E (electromotive force) or V
  – Analogy: water pressure in a pipe — more pressure, more push
■ Voltage is always measured BETWEEN two points (a potential difference)
  – A bird on one wire sits at one potential — no difference, no current
  – Bridge two different potentials and current flows through you
■ Higher voltage can push current across larger air gaps — it can arc to you before you touch it
KEY CONCEPT
Why this matters
– Every safe-work distance exists because voltage can drive current across air.
– “Difference of potential” is the whole game — control it and you control the hazard.
Module 1 — Electrical Theory
Powerline Electrical Theory & Safety | 08

## Slide 9
1.4 CURRENT
Current — The Flow That Hurts You
■ Current (I) is the rate of charge flow, measured in amperes (amps)
  – Analogy: the volume of water flowing past a point
■ It is CURRENT through the body — not voltage — that injures and kills
  – Voltage determines how much current will be pushed through your resistance
■ Even small currents across the chest can stop the heart
■ Fault current on distribution/transmission can be thousands of amps
  – Enough to vaporize metal and create an arc-flash explosion
DANGER ⚠
Remember
– It takes surprisingly little current to be fatal.
– Milliamps through the heart — not amps — are deadly.
– Protect against the current by removing the path and the potential difference.
Module 1 — Electrical Theory
Powerline Electrical Theory & Safety | 09

## Slide 10
1.5 OHM'S LAW
Resistance, Ohm's Law & Power
Three quantities, one relationship — the most useful equation you will ever memorize.
■ Resistance (R) opposes current flow — measured in ohms (Ω)
  – Conductors = low R; insulators = high R; your skin's R drops sharply when wet
■ Ohm's Law ties the three together: V = I × R
  – Current I = V / R → same voltage + lower body resistance = MORE current through you
  – This is why sweat, water, and broken skin make a shock far more dangerous
■ Power is the rate of doing work — measured in watts: P = V × I
  – Also P = I² × R — heat in a fault rises with the SQUARE of current
  – That heat is what drives burns and arc-flash energy
■ Utilities sell energy in kilowatt-hours (kWh): power used over time
Module 1 — Electrical Theory
Powerline Electrical Theory & Safety | 10

## Slide 11
1.5 REFERENCE
The Ohm's Law / Power Wheel — Quick Reference
To find | If you know | Use the formula | Units
Voltage (E) | Current & Resistance | E = I × R | Volts (V)
Current (I) | Voltage & Resistance | I = E ÷ R | Amperes (A)
Resistance (R) | Voltage & Current | R = E ÷ I | Ohms (Ω)
Power (P) | Voltage & Current | P = E × I | Watts (W)
Power (P) | Current & Resistance | P = I² × R | Watts (W)
Power (P) | Voltage & Resistance | P = E² ÷ R | Watts (W)
Tip: cover the value you want in the V / I / R triangle and the remaining two show you the operation. Power = the rate energy is delivered — and the source of heat and arc energy.
Module 1 — Electrical Theory
Powerline Electrical Theory & Safety | 11

## Slide 12
1.6 WAVEFORMS
AC vs DC
Direct Current (DC)
■ Electrons flow one direction only
■ Batteries, solar arrays, some traction & HVDC systems
■ Steady polarity — + and – stay fixed
■ Cannot be easily transformed up/down in voltage
■ DC can cause sustained muscle 'lock-on'
Alternating Current (AC)
■ Electrons reverse direction cyclically
■ 60 Hz in North America = 60 cycles per second
■ Polarity and magnitude change continuously (a sine wave)
■ Easily stepped up/down by transformers — why the grid uses it
■ Crosses zero 120×/sec, but is still lethal — never assume 'off'
Module 1 — Electrical Theory
Powerline Electrical Theory & Safety | 12

## Slide 13
1.6 AC BEHAVIOR
AC Details: Frequency, Peak & RMS
■ One full cycle = one complete positive + negative swing of the sine wave
■ Frequency = cycles per second, measured in hertz (Hz); 60 Hz in the U.S./Canada
■ Peak voltage is the maximum the wave reaches; the average useful value is the RMS
  – RMS (root-mean-square) is the 'DC-equivalent' value — it does the same work
  – When we say 120 V or 7,200 V, we mean RMS; peak is ~1.414× higher
■ Phase describes where two AC waveforms are in their cycle relative to each other
  – Critical for three-phase systems and for paralleling sources
■ Inductance and capacitance on lines cause current and voltage to shift out of step
  – This is the source of INDUCED voltage on de-energized parallel circuits (Module 3)
Module 1 — Electrical Theory
Powerline Electrical Theory & Safety | 13

## Slide 14
1.7 PHASES
Single-Phase vs Three-Phase
Single-Phase
■ One AC voltage waveform (with neutral)
■ Typical residential service: 120/240 V
■ Simple loads — lighting, receptacles, small motors
■ Power delivery pulses (crosses zero each half-cycle)
Three-Phase
■ Three waveforms 120° apart — A, B, C phases
■ Backbone of transmission, distribution & industrial power
■ Smooth, continuous power — efficient for large motors
■ More power in less conductor than single-phase
■ Phase-to-phase voltage = √3 (1.732) × phase-to-neutral
Module 1 — Electrical Theory
Powerline Electrical Theory & Safety | 14

## Slide 15
1.8 TRANSFORMERS
Transformers — Stepping Voltage Up & Down
The single reason the grid runs on AC — voltage can be transformed efficiently.
■ A transformer changes AC voltage using two coils linked by a magnetic core
  – No direct electrical connection — energy crosses by induction
■ Turns ratio sets the voltage ratio: more secondary turns → higher voltage
  – Step UP: raise voltage for transmission (less current = less line loss)
  – Step DOWN: lower voltage for distribution and the customer
■ Power in ≈ power out, so when voltage goes UP, current goes DOWN (and vice-versa)
  – P = V × I — this is WHY we transmit at high voltage: to cut I²R losses
■ Distribution transformers on the pole/pad drop primary (e.g., 7,200 V) to 120/240 V
■ WARNING: a de-energized secondary can be BACK-FED from the customer side — generators!
Module 1 — Electrical Theory
Powerline Electrical Theory & Safety | 15

## Slide 16
1.9 THE SYSTEM
The Grid: From Generation to Your Service
Know where you are on this chain — it tells you the voltage, the fault energy, and the controls you need.
1
1. Generation
Power plants (gas, hydro, nuclear, wind, solar) produce AC, typically at medium voltage.
2
2. Step-Up Substation
Transformers raise voltage to transmission levels (69 kV up to 765 kV) to move power far with low loss.
3
3. Transmission Lines
High-voltage lines on large towers carry bulk power across regions.
4
4. Step-Down / Distribution Substation
Voltage is reduced to distribution levels (typically 4 kV–35 kV).
5
5. Distribution Feeders
Primary lines on poles carry power through neighborhoods; reclosers & fuses protect them.
6
6. Service Transformer & Customer
Final step-down to 120/240 V (residential) or higher for commercial/industrial.
Module 1 — Electrical Theory
Powerline Electrical Theory & Safety | 16

## Slide 17
1.10 VOLTAGE CLASSES
Voltage Classes You Will Work Around
Class | Typical Range | Where you see it | Note
Low voltage | < 600 V | Services, secondary, street light | Still deadly — most contacts happen here
Medium voltage (Distribution) | 600 V – 35 kV | Primary feeders, urban/rural lines | Common lineworker environment
High voltage (Sub-transmission/Transmission) | 35 kV – 230 kV | Towers, large substations | Larger MAD; arc & induction hazards grow
Extra-high voltage (EHV) | 230 kV – 765 kV | Bulk transmission | Specialized live-line methods, large clearances
Ultra-high voltage (UHV) | > 765 kV | Long-distance bulk corridors | Rare; highly specialized work
Exact class boundaries vary by utility and standard (NESC/IEEE). What never changes: higher voltage = larger required clearances and greater fault energy.
Module 1 — Electrical Theory
Powerline Electrical Theory & Safety | 17

## Slide 18
ILLUSTRATED
How Electricity Flows
Electrons drifting from atom to atom — driven by a difference in charge — are electric current.
Module 1 — Electrical Theory
Powerline Electrical Theory & Safety | 18

## Slide 19
ILLUSTRATED
Conductors vs Insulators
Conductors let electrons pass (low resistance); insulators bind them (high resistance).
Module 1 — Electrical Theory
Powerline Electrical Theory & Safety | 19

## Slide 20
ILLUSTRATED
The Water Analogy
Voltage is pressure, current is flow, resistance is the restriction: I = V ÷ R.
Module 1 — Electrical Theory
Powerline Electrical Theory & Safety | 20

## Slide 21
ILLUSTRATED
Why Voltage Needs Two Points
One potential is safe; bridging two different potentials drives current through you.
Module 1 — Electrical Theory
Powerline Electrical Theory & Safety | 21

## Slide 22
ILLUSTRATED
The Ohm's Law & Power Wheel
Cover the unknown in the V / I / R triangle. Power P = V×I = I²R — heat rises with current squared.
Module 1 — Electrical Theory
Powerline Electrical Theory & Safety | 22

## Slide 23
ILLUSTRATED
AC vs DC Waveforms
DC flows one way at a steady level; AC reverses 60×/sec, which lets transformers change its voltage.
Module 1 — Electrical Theory
Powerline Electrical Theory & Safety | 23

## Slide 24
ILLUSTRATED
Three-Phase Power
Three waveforms 120° apart deliver smooth, continuous power — the backbone of the grid.
Module 1 — Electrical Theory
Powerline Electrical Theory & Safety | 24

## Slide 25
ILLUSTRATED
How a Transformer Works
Two coils on a magnetic core: the turns ratio sets the voltage ratio; power in ≈ power out.
Module 1 — Electrical Theory
Powerline Electrical Theory & Safety | 25

## Slide 26
ILLUSTRATED
The Grid, End to End
Voltage is stepped up for transmission, then down in stages until it is safe for the customer.
Module 1 — Electrical Theory
Powerline Electrical Theory & Safety | 26

## Slide 27
MODULE 1 RECAP
Module 1 — Key Takeaways
■ Electricity is the flow of charge that always wants to return to its source via every path
■ Voltage pushes; current flows; resistance opposes — V = I × R ties them together
■ It is CURRENT through the body that kills, and low body resistance lets more through
■ AC dominates the grid because transformers let us change voltage efficiently
■ Transmit high (low current, low loss); distribute and use low (safe for customers)
■ Know your voltage class — it sets your clearances, fault energy, and controls
Module 1 — Electrical Theory
Powerline Electrical Theory & Safety | 27

## Slide 28
MODULE
2
Electricity & the Human Body
— How current injures and kills
— Shock thresholds & the heart
— Electrical burns
— Arc flash and arc blast
— Step, touch & ground-gradient potential

## Slide 29
2.1 SHOCK PHYSIOLOGY
How Current Affects the Body
■ The body is a conductor — nerves and muscles run on tiny electrical signals
■ External current overrides those signals: muscles clamp, nerves misfire, the heart can fibrillate
■ Severity depends on:
  – Amount of current (the key factor) — set by voltage ÷ your resistance
  – Path through the body — hand-to-hand or hand-to-foot crosses the heart
  – Duration of contact — longer exposure, more damage
  – Frequency — 60 Hz AC is especially effective at causing fibrillation
■ Skin resistance can be ~100,000 Ω dry, but drops to ~1,000 Ω or less when wet/broken
  – Same voltage then drives far more current — wet conditions are a force multiplier
Module 2 — Electricity & the Body
Powerline Electrical Theory & Safety | 29

## Slide 30
2.2 THRESHOLDS
Approximate Effects of 60 Hz Current Across the Body
Current (through body) | Typical effect
~1 mA | Threshold of perception — a faint tingle
~5 mA | Slight shock; not painful but startling — can cause falls
6–16 mA | Painful shock; loss of muscular control begins (“let-go” threshold)
17–20 mA | Muscles clamp — CANNOT let go of the conductor; breathing labored
20–50 mA | Severe muscle contractions, breathing difficulty
50–100 mA | Possible ventricular fibrillation — the heart quivers, stops pumping
100 mA – 2 A | Likely fatal ventricular fibrillation; nerve damage
> 2 A | Cardiac arrest, severe internal burns, organ damage
Values are approximate and vary by body size, path, and conditions. The lesson: the dangerous range starts in the MILLIAMP region — far below what trips most circuits.
Module 2 — Electricity & the Body
Powerline Electrical Theory & Safety | 30

## Slide 31
2.3 THE HEART
The Heart, Let-Go & Fibrillation
■ “Let-go threshold”: above ~10–16 mA your flexor muscles clamp and you cannot release the conductor
  – The longer you hold on, the more the contact heats and the more current flows
■ Ventricular fibrillation: current disrupts the heart's rhythm so it quivers instead of pumping
  – Blood stops circulating — brain damage in minutes, death without intervention
  – A defibrillator/AED and CPR may restart a coordinated rhythm — know where yours is
■ Even a 'minor' shock can throw you from a pole or bucket — the fall often does the damage
DANGER ⚠
Why we never rely on 'holding on'
– Above the let-go threshold your body works against you.
– The only safe contact with an energized conductor is NO direct contact — insulate and isolate.
Module 2 — Electricity & the Body
Powerline Electrical Theory & Safety | 31

## Slide 32
2.4 BURNS
Electrical Burns
How they happen
■ Contact / true electrical burns: current flowing through tissue generates heat (I²R)
■ Arc burns: radiated heat from an arc — can exceed 35,000°F at the arc
■ Thermal-contact burns: ignited clothing or hot surfaces
■ Flash burns to eyes (welder's flash) from intense UV
Why they are deceptive
■ Entry/exit wounds may look small but mask massive internal damage
■ Current cooks tissue along its whole path — nerves, muscle, organs
■ Delayed effects: kidney damage from tissue breakdown, cardiac issues
■ ALWAYS seek medical evaluation after any electrical contact — even if you feel fine
Module 2 — Electricity & the Body
Powerline Electrical Theory & Safety | 32

## Slide 33
2.5 ARC FLASH
Arc Flash & Arc Blast
■ An arc flash is an explosive release of energy when current jumps through ionized air
  – Triggered by faults, dropped tools, animals, equipment failure, or getting too close
■ Arc FLASH = light & heat: temperatures up to ~35,000°F (hotter than the sun's surface)
■ Arc BLAST = pressure wave: vaporized metal expands violently
  – Copper expands ~67,000 times when it vaporizes — like a small explosion
  – Concussive force, shrapnel, molten metal spray, sound > 140 dB
■ Incident energy is measured in cal/cm² — it sets the arc rating of PPE you must wear
DANGER ⚠
Controlled by
– Distance (clearances), de-energizing, and arc-rated FR clothing/face protection.
– An arc flash can occur WITHOUT you touching anything — proximity alone can trigger it.
Module 2 — Electricity & the Body
Powerline Electrical Theory & Safety | 33

## Slide 34
2.6 GROUND GRADIENTS
Step Potential & Touch Potential
■ When current flows into the earth (e.g., a downed line, a fault to a ground rod), it spreads out
■ Voltage drops with distance from the contact point — forming a 'voltage gradient' across the ground
■ STEP POTENTIAL: the voltage difference between your two feet
  – One foot sits at a higher potential than the other — current flows up one leg, down the other
  – The wider your stride, the greater the difference — and the greater the shock
■ TOUCH POTENTIAL: difference between your hand (on an object) and your feet
  – Touching a faulted structure while standing on ground at a different potential
DANGER ⚠
If you must leave an energized area
– Keep feet together and SHUFFLE or bunny-hop — never take a normal stride.
– Assume the ground around any downed line is energized out to a wide radius.
– Equipotential bonding & grounding (Module 3) eliminate these gradients in your work zone.
Module 2 — Electricity & the Body
Powerline Electrical Theory & Safety | 34

## Slide 35
2.7 DOWNED LINES
Downed Conductors & The Ground Around You
The most dangerous ground is the ground that looks perfectly normal.
■ A downed line may look dead — it is NOT until tested and grounded
  – It may be re-energized automatically by reclosers, or back-fed by a customer's generator
■ Energized ground can extend many feet from the contact point — you cannot see it
■ Vehicles in contact with lines: occupants should STAY INSIDE unless fire forces evacuation
  – If they must exit: JUMP clear without touching vehicle and ground at once, then shuffle away
■ Keep the public back — establish a wide barrier and treat everything as energized
■ Never approach within the established radius until the line is confirmed de-energized & grounded
Module 2 — Electricity & the Body
Powerline Electrical Theory & Safety | 35

## Slide 36
ILLUSTRATED
Current Path Through the Body
Current across the chest — hand-to-hand or hand-to-foot — can stop the heart. Control both contact points.
Module 2 — Electricity & the Body
Powerline Electrical Theory & Safety | 36

## Slide 37
ILLUSTRATED
Shock Threshold Ladder
The dangerous range begins in milliamps — far below what trips a typical breaker.
Module 2 — Electricity & the Body
Powerline Electrical Theory & Safety | 37

## Slide 38
ILLUSTRATED
Arc Flash & Arc Blast
An arc can reach ~35,000°F with an explosive blast — and can be triggered by proximity alone.
Module 2 — Electricity & the Body
Powerline Electrical Theory & Safety | 38

## Slide 39
ILLUSTRATED
Step & Touch Potential
Current spreading from a downed line creates a ground gradient. Shuffle out with feet together.
Module 2 — Electricity & the Body
Powerline Electrical Theory & Safety | 39

## Slide 40
ILLUSTRATED
Reclosers — Why a Dead Line Bites Back
Reclosers trip then auto-reclose — a downed line can re-energize without warning.
Module 2 — Electricity & the Body
Powerline Electrical Theory & Safety | 40

## Slide 41
MODULE 2 RECAP
Module 2 — Key Takeaways
■ Current — not voltage — injures; the dangerous range begins in milliamps
■ Path across the heart and 60 Hz AC make fibrillation likely; wet skin worsens everything
■ Above the let-go threshold you cannot release — so we never rely on letting go
■ Arc flash/blast can kill or maim WITHOUT contact — distance and FR PPE are your defense
■ Energized ground creates step & touch potential — shuffle out, bond and ground your zone
■ After any contact: get medical evaluation — internal damage hides
Module 2 — Electricity & the Body
Powerline Electrical Theory & Safety | 41

## Slide 42
MODULE
3
Working Around Energized Lines & Equipment
— Minimum approach distance
— The second point of contact — the core concept
— Isolate, insulate & cover-up
— Grounding & the equipotential zone
— De-energizing, LOTO & induced voltage

## Slide 43
3.1 CONTROLS
The Hierarchy of Controls for Electrical Work
Reach for the top of the hierarchy first; PPE alone is never the plan.
■ The safest energized work is work that isn't energized — always prefer de-energizing where feasible
■ Order of preference when planning a job:
  – 1. Eliminate — de-energize, isolate, lock & tag, test dead, and ground
  – 2. Substitute / engineer — reroute, switch load, use remote/robotic methods
  – 3. Isolate the worker — insulate & isolate (rubber-glove or hot-stick / live-line bare-hand)
  – 4. Administrative — procedures, job briefings, MAD, qualified workers only
  – 5. PPE — FR clothing, rubber gloves/sleeves, face & head protection (last line, never the only line)
■ Energized work is permitted only when de-energizing is infeasible or creates greater hazard
Module 3 — Working Energized
Powerline Electrical Theory & Safety | 43

## Slide 44
3.2 MAD
Minimum Approach Distance (MAD)
■ MAD = the closest a qualified worker (or conductive object) may come to an energized part
■ It protects against flashover — the air gap that voltage cannot jump
■ MAD increases with voltage and with altitude (thinner air insulates less)
■ It includes the phase-to-ground AND phase-to-phase exposure
■ Anything conductive counts: your body, tools, materials, the boom, a tape measure
  – Unqualified employees must stay even farther back
■ If you cannot maintain MAD, the part must be de-energized OR covered/insulated
WARNING ⚠
Rule of thumb
– Know your utility's MAD table for the voltage you're on — BEFORE you leave the ground.
– When in doubt, cover up or back off. MAD is a minimum, not a target.
Module 3 — Working Energized
Powerline Electrical Theory & Safety | 44

## Slide 45
3.2 MAD TABLE
Illustrative Minimum Approach Distances (Phase-to-Ground)
Nominal Voltage (ph-ph) | Example MAD | Typical Setting
50 V – 300 V | Avoid contact | Service / secondary
301 V – 750 V | ~1 ft 1 in | Secondary / street light
751 V – 15 kV | ~2 ft 2 in | Distribution primary
15.1 kV – 36 kV | ~2 ft 7 in | Distribution / sub-transmission
36.1 kV – 46 kV | ~2 ft 9 in | Sub-transmission
46.1 kV – 72.5 kV | ~3 ft 3 in | Sub-transmission
72.6 kV – 121 kV | ~3 ft 4 in | Transmission
138 kV – 145 kV | ~3 ft 7 in | Transmission
230 kV | ~5 ft 3 in | Bulk transmission
ILLUSTRATIVE ONLY — distances vary with altitude, transient over-voltage factor, and the governing edition of OSHA 1910.269 Table R-3 / R-6. ALWAYS use your employer's current, approved MAD table.
Module 3 — Working Energized
Powerline Electrical Theory & Safety | 45

## Slide 46
3.3 SECOND POINT OF CONTACT
The Second Point of Contact — The Concept That Saves Lives
■ Current can only flow when it has a complete path: a source, a load/body, and a return
■ Touching ONE energized conductor while perfectly insulated from everything else = no path
  – This is why a bird sits on a wire unharmed — it is at one potential, with no second contact
■ The SECOND POINT OF CONTACT is what completes the circuit through you:
  – A grounded neutral, a guy wire, a pole ground, a crossarm, the structure
  – Another phase at a different potential (phase-to-phase — even more dangerous)
  – A co-worker, a tool, the bucket, a wet rope, the truck
■ Eliminate the second point of contact and you eliminate the shock — every time
DANGER ⚠
The discipline
– Before you reach for ANY energized part, ask: 'Where is my second point of contact?'
– Cover it. Insulate it. Or remove yourself from it.
– Most electrocutions are NOT phase-to-phase — they are phase-to-GROUND through a missed second point.
Module 3 — Working Energized
Powerline Electrical Theory & Safety | 46

## Slide 47
3.3 APPLICATION
Finding Your Second Point of Contact — Every Time
Rubber gloves alone are not the answer — you must also control what else you could touch.
■ Scan the whole work envelope, not just the conductor you're working
■ Common second points hiding in plain sight:
  – Grounded neutral conductor (often the closest deadly path)
  – The pole ground / ground wire, guy wires and down-guys
  – Metal crossarm braces, bolts, staples, hardware
  – Other phases above, below, or behind you
  – Transformer cases, capacitor banks, riser/cable terminations
  – The bucket lip, jib, winch line, hand line, or another worker
■ Work to keep yourself, your tools, and the energized part isolated from all of them
■ Glove AND cover: rubber gloves protect your hands; cover-up protects against the SECOND point
Module 3 — Working Energized
Powerline Electrical Theory & Safety | 47

## Slide 48
3.4 TWO METHODS
Insulate & Isolate — The Two Methods of Protection
■ INSULATE: place insulating barriers between the worker and energized/grounded parts
  – Rubber gloves, sleeves, line hose, hoods, blankets — rated for the voltage
  – Insulated tools and platforms; the dielectric boom of an aerial device
■ ISOLATE: create distance/separation so no path can form
  – Maintain MAD; reposition the work; use live-line (hot-stick) tools to keep the worker back
■ Rubber-glove method: worker is insulated and works within reach — cover-up is mandatory
■ Hot-stick / live-line tool method: worker stays beyond MAD and works through tools
■ Bare-hand (live-line) method: worker is bonded TO the conductor at line potential — specialized, EHV
Module 3 — Working Energized
Powerline Electrical Theory & Safety | 48

## Slide 49
3.5 COVER-UP
Cover-Up: Purpose & Principles
Cover-up turns a cluttered, energized pole top into an isolated, defendable work zone.
■ Cover-up = installing insulating guards over energized AND grounded parts in the work zone
■ Purpose: protect against accidental contact and eliminate second points of contact
  – It is secondary protection — it backs up your gloves, MAD, and positioning
■ Cover EVERYTHING within reach you could contact: phases, neutral, ground, hardware, guys
■ Cover-up must be rated for the system voltage and inspected before use
■ Install from a position of safety — nearest/most-accessible energized part first, working outward
  – Use a hot stick or gloved hands per procedure; never let cover-up create a false sense of security
■ Remove in REVERSE order — last on, first off — keeping protection in place longest where you work
Module 3 — Working Energized
Powerline Electrical Theory & Safety | 49

## Slide 50
3.5 SEQUENCE
Cover-Up Sequence — Building the Protected Zone
1
1. Plan & inspect
Identify every energized & grounded part within reach. Inspect all cover-up for damage; verify voltage rating.
2
2. Establish footing
Position the bucket/yourself so you can reach with the conductor at a safe angle — from below where possible.
3
3. Cover the closest hazard first
Apply line hose/blankets to the nearest energized phase, then work outward to additional phases.
4
4. Cover the second points
Cover the neutral, ground wire, guys, crossarm hardware — anything that could be your second point of contact.
5
5. Work the job
With the zone insulated, perform the task maintaining gloves, MAD, and positioning throughout.
6
6. Remove in reverse
Strip cover-up last-on/first-off — keep protection nearest you in place until the end.
Module 3 — Working Energized
Powerline Electrical Theory & Safety | 50

## Slide 51
3.5 EQUIPMENT
Cover-Up Equipment
Types of cover-up
■ Line hose — tubular cover for conductors
■ Insulator hoods — cover pin/post insulators & tops
■ Conductor/line covers & connector covers
■ Insulating blankets — wrap irregular shapes, hardware
■ Dead-end & pole/crossarm covers, guy guards
Selection & care
■ Match the voltage rating to (or above) the system
■ Inspect for cuts, ozone cracks, embedded metal, swelling
■ Keep clean & dry; store properly — no sharp folds
■ Use approved clip pins/connectors so it stays put
■ Removed from service & retested per schedule if suspect
Module 3 — Working Energized
Powerline Electrical Theory & Safety | 51

## Slide 52
3.6 DE-ENERGIZE / LOTO
De-Energizing & Lockout/Tagout (LOTO)
■ When a line can be de-energized, follow the formal switching & clearance procedure
■ The classic verification sequence — do not skip a step:
  – 1. Identify the correct circuit/section (right line, right structure)
  – 2. Open the disconnects and render them visibly open
  – 3. Lock and TAG the points of isolation — each worker's own lock
  – 4. TEST for absence of voltage with a tested-good detector (test-before-touch)
  – 5. Apply protective GROUNDS to create an equipotential, drained zone
■ Hold the clearance; only the holder releases it after all workers are clear
WARNING ⚠
Test your tester
– Prove the voltage detector works on a known source BEFORE and AFTER testing the line.
– Treat every conductor as energized until YOU have verified it dead and grounded.
Module 3 — Working Energized
Powerline Electrical Theory & Safety | 52

## Slide 53
3.7 GROUNDING & EPZ
Grounding & The Equipotential Zone
■ Protective grounding does NOT just 'drain' the line — it protects YOU if it is re-energized
■ If the line is accidentally energized, grounds provide a low-resistance path that trips protection fast
■ Equipotential zone (EPZ): bond everything you could touch to the SAME potential
  – If everything around you is at the same voltage, no current flows through you — like the bird
■ Bonding: connect conductors, structures, and equipment together; ground that bonded system
■ Grounds must be sized for available fault current and connected in the correct order
  – Connect to ground/structure FIRST, then to the conductor; remove in REVERSE
KEY CONCEPT
Why grounds save lives
– A worker inside a properly bonded EPZ rides the voltage up and down together — no difference of potential across the body.
– Grounds are sized to carry fault current long enough for the breaker/recloser to operate.
Module 3 — Working Energized
Powerline Electrical Theory & Safety | 53

## Slide 54
3.8 INDUCED VOLTAGE
Induced Voltage — The Hidden Hazard on 'Dead' Lines
“Dead” is not the same as “grounded.” Induction is why we ground at the work location.
■ A de-energized line running parallel to an energized one can pick up voltage by induction
  – Magnetic (current) and electrostatic (voltage) coupling from the live circuit
■ The longer the parallel and the higher the live circuit's load, the greater the induced voltage
■ An ungrounded 'dead' line can hold enough induced potential to shock or kill
■ Control it by GROUNDING — and by working within a bonded equipotential zone
  – Grounds at the work site (not just at the ends) keep induced potential off the worker
■ Switching, transmission, and parallel-circuit work demand extra attention to induction
Module 3 — Working Energized
Powerline Electrical Theory & Safety | 54

## Slide 55
ILLUSTRATED
The Hierarchy of Controls
Work from the top down: de-energize first; PPE is the last line, never the only line.
Module 3 — Working Energized
Powerline Electrical Theory & Safety | 55

## Slide 56
ILLUSTRATED
Minimum Approach Distance
Keep body, tools, and equipment outside the minimum approach distance for your voltage.
Module 3 — Working Energized
Powerline Electrical Theory & Safety | 56

## Slide 57
ILLUSTRATED
The Insulated Aerial Device
The fiberglass upper boom is a dielectric insulating gap between the bucket and ground.
Module 3 — Working Energized
Powerline Electrical Theory & Safety | 57

## Slide 58
ILLUSTRATED
The Second Point of Contact
Eliminate the second point of contact — cover it or remove it — and the circuit can't close through you.
Module 3 — Working Energized
Powerline Electrical Theory & Safety | 58

## Slide 59
ILLUSTRATED
Cover-Up at the Pole Top
Insulate every energized and grounded part within reach: nearest first, remove in reverse.
Module 3 — Working Energized
Powerline Electrical Theory & Safety | 59

## Slide 60
ILLUSTRATED
The De-Energize / LOTO Sequence
Identify → open → lock & tag → test → ground. Never skip a step.
Module 3 — Working Energized
Powerline Electrical Theory & Safety | 60

## Slide 61
ILLUSTRATED
The Equipotential Zone
Bond and ground a work zone to one potential — no difference across the body means no current.
Module 3 — Working Energized
Powerline Electrical Theory & Safety | 61

## Slide 62
ILLUSTRATED
How Induced Voltage Appears
A parallel live line couples voltage onto a dead one — ground at the work site, not just the ends.
Module 3 — Working Energized
Powerline Electrical Theory & Safety | 62

## Slide 63
MODULE 3 RECAP
Module 3 — Key Takeaways
■ Prefer de-energizing; when working hot, isolate AND insulate — never rely on one control
■ Maintain MAD for your voltage; anything conductive counts toward the distance
■ THE SECOND POINT OF CONTACT completes the circuit — find it, cover it, remove it, every time
■ Cover-up backs up your gloves and MAD: nearest first, remove in reverse
■ De-energize properly: identify, open, lock/tag, TEST, then GROUND
■ Bond an equipotential zone and ground at the work site — it defeats re-energization AND induction
Module 3 — Working Energized
Powerline Electrical Theory & Safety | 63

## Slide 64
MODULE
4
Tools of the Trade
— Rubber insulating gloves & sleeves
— Live-line (hot-stick) tools
— Protective grounds & testers
— Arc-rated FR clothing & PPE
— Inspection, testing & care

## Slide 65
4.1 RUBBER GLOVES
Rubber Insulating Gloves — Your First Line of Defense
■ Rubber gloves insulate your hands from energized parts in the rubber-glove method
■ Always worn with leather protector gloves OVER them
  – The leather shields the rubber from cuts, abrasion, and UV — the rubber does the insulating
■ Selected by VOLTAGE CLASS — each class has a max use voltage and proof-test voltage
■ Field-inspect before EVERY use:
  – Air-test (roll/inflate) to find pinholes; check for cuts, cracks, swelling, embedded debris
  – Inspect inside and out; check for chemical or ozone damage
■ Retest electrically on a schedule (typically every 6 months) at a certified lab
■ Store in a glove bag, fingers up, away from heat, ozone, sunlight, and sharp objects
Module 4 — Tools of the Trade
Powerline Electrical Theory & Safety | 65

## Slide 66
4.1 GLOVE CLASSES
Rubber Glove Voltage Classes (ASTM D120 / IEC)
Class | Max Use Voltage (AC, ph-ph) | Color (label) | Proof Test
Class 00 | 500 V | Beige | 2,500 V
Class 0 | 1,000 V | Red | 5,000 V
Class 1 | 7,500 V | White | 10,000 V
Class 2 | 17,000 V | Yellow | 20,000 V
Class 3 | 26,500 V | Green | 30,000 V
Class 4 | 36,000 V | Orange | 40,000 V
Always select a class rated AT or ABOVE the maximum voltage you may contact. Label color aids quick identification; the printed rating governs. Same class system applies to insulating sleeves and many blankets.
Module 4 — Tools of the Trade
Powerline Electrical Theory & Safety | 66

## Slide 67
4.2 SLEEVES & COVER
Rubber Sleeves, Blankets & Line Hose
Sleeves
■ Insulate the forearm, upper arm, and shoulder
■ Worn when the arm could contact an energized/grounded part
■ Same voltage-class system as gloves
■ Inspected & retested like gloves
Blankets & line hose
■ Blankets: flexible cover for irregular shapes & hardware
■ Line hose: slips over conductors to insulate runs
■ Secured with approved pins/snaps/clamps
■ Voltage-rated; inspected for cuts, ozone & contamination
Module 4 — Tools of the Trade
Powerline Electrical Theory & Safety | 67

## Slide 68
4.3 HOT STICKS
Live-Line (Hot-Stick) Tools
A hot stick keeps the worker back while the work goes forward — isolation in tool form.
■ Hot sticks are insulating tools (usually fiberglass/epoxy) that extend your reach beyond MAD
■ Let qualified workers operate, test, install and remove equipment without closing the gap
■ Common types:
  – Universal / shotgun (telescoping) sticks with interchangeable heads
  – Switch sticks, disconnect sticks, fuse pullers
  – Tie sticks, wire-holding & cleaning tools, measuring sticks
  – Grounding sticks (clamp sticks) for applying protective grounds
■ Keep them CLEAN and DRY — contamination & moisture ruin the insulating surface
  – Wipe down with an approved cleaner/wax; use a cradle, not the ground
■ Inspect for scratches, cracks, soft spots; periodic dielectric testing required
Module 4 — Tools of the Trade
Powerline Electrical Theory & Safety | 68

## Slide 69
4.4 GROUNDS
Protective Grounds & Grounding Equipment
■ Personal protective grounds = flexible copper cables with clamps (ferrules) and ground studs
■ Sized to carry the available fault current for the clearing time without failing
  – Undersized grounds can fuse and fail under fault — use the correct cable size
■ Components: cable, clamps, ferrules, ground rods/cluster bars, EPZ jumpers
■ Apply correctly: clean contact points, tight clamps, ground end FIRST then line end
■ Use grounding sticks to install/remove — treat the line as energized until grounds are on
■ Inspect for broken strands, corroded clamps, loose ferrules; remove damaged sets from service
■ Remove grounds in REVERSE: line end first, ground end last
Module 4 — Tools of the Trade
Powerline Electrical Theory & Safety | 69

## Slide 70
4.5 TESTERS
Voltage Detectors & Testers
Types
■ Contact voltage detectors (on a hot stick)
■ Non-contact / proximity testers (presence of field)
■ Phasing testers — verify phase relationships
■ Audible/visual indication of energized condition
Use it right
■ TEST the tester on a known source before AND after
■ Match the detector's range to the system voltage
■ Test-before-touch on every conductor, every time
■ A 'no voltage' reading from an unproven tester proves NOTHING
Module 4 — Tools of the Trade
Powerline Electrical Theory & Safety | 70

## Slide 71
4.6 FR / PPE
Arc-Rated FR Clothing & Personal PPE
■ Flame-resistant (FR) / arc-rated (AR) clothing protects against arc-flash thermal energy
  – Rated in cal/cm² (ATPV / arc rating) — must meet or exceed the job's incident energy
  – Self-extinguishing; will not melt and drip like synthetics (no untreated nylon/poly next to skin)
■ Layering increases protection; outermost layer must be arc-rated
■ Head/face/eyes: hard hat (Class E, electrical), arc-rated face shield/hood, safety glasses
■ Hands: rubber gloves + leather protectors; feet: EH-rated footwear
■ Hearing protection for arc-blast environments; no exposed conductive jewelry
■ PPE is the LAST layer — it limits injury when other controls fail; it never replaces them
Module 4 — Tools of the Trade
Powerline Electrical Theory & Safety | 71

## Slide 72
4.7 INTERVALS
PPE & Tool Inspection / Test Intervals (Typical)
Item | Before each use | Periodic electrical test
Rubber gloves | Air & visual inspection | Retest ≈ every 6 months
Rubber sleeves | Visual inspection | Retest ≈ every 6 months
Insulating blankets | Visual inspection | Retest ≈ every 12 months
Line hose / covers | Visual inspection | When suspect / per program
Hot sticks / live-line tools | Wipe & visual inspection | Periodic dielectric test (e.g., every 2 yrs)
Protective grounds | Visual; check clamps/strands | Resistance/condition per program
Voltage detectors | Self-test before & after use | Per manufacturer schedule
FR clothing | Inspect for damage/contamination | Replace when worn/contaminated
Intervals are TYPICAL and governed by OSHA 1910.137, ASTM F496/F478, and your employer's program. If equipment is dropped, suspect, or out of test date — remove it from service.
Module 4 — Tools of the Trade
Powerline Electrical Theory & Safety | 72

## Slide 73
ILLUSTRATED
Rubber Glove Voltage Classes
Select a glove class rated at or above your system voltage; wear leather protectors over them.
Module 4 — Tools of the Trade
Powerline Electrical Theory & Safety | 73

## Slide 74
ILLUSTRATED
The Live-Line (Hot-Stick) Method
A fiberglass live-line tool extends reach beyond MAD — keep it clean and dry.
Module 4 — Tools of the Trade
Powerline Electrical Theory & Safety | 74

## Slide 75
ILLUSTRATED
Phasing & Voltage Testing
Verify voltage and phase — and prove the tester on a known source before and after.
Module 4 — Tools of the Trade
Powerline Electrical Theory & Safety | 75

## Slide 76
ILLUSTRATED
Protective Grounding Sets
Grounds carry fault current and trip protection fast: ground end first, line ends last.
Module 4 — Tools of the Trade
Powerline Electrical Theory & Safety | 76

## Slide 77
ILLUSTRATED
Head-to-Toe PPE
Arc-rated FR clothing, Class E hard hat, face shield, rubber gloves — the last layer of defense.
Module 4 — Tools of the Trade
Powerline Electrical Theory & Safety | 77

## Slide 78
MODULE 4 RECAP
Module 4 — Key Takeaways
■ Rubber gloves (with leather protectors) are first-line insulation — selected by voltage class
■ Air-test and inspect rubber goods before every use; honor retest dates
■ Hot sticks isolate the worker; grounds protect against re-energization — both must be tested & sized
■ Test your tester before AND after; test-before-touch every time
■ Arc-rated FR PPE must meet or exceed the incident energy — and it's the last layer, not the plan
■ Clean, dry, inspected, in-date — or out of service. No exceptions.
Module 4 — Tools of the Trade
Powerline Electrical Theory & Safety | 78

## Slide 79
MODULE
5
Putting It to Work in the Field
— Pre-job planning
— Hazard assessment / JSA
— The tailboard / job briefing
— Roles, responsibilities & communication
— Emergency response & rescue

## Slide 80
5.1 PLANNING
Pre-Job Planning — Before Boots Leave the Truck
■ Understand the SCOPE: what work, on what equipment, at what voltage, energized or not
■ Review prints, switching orders, clearances, and the circuit map
■ Confirm the right crew, qualifications, and a competent person in charge
■ Verify tools, PPE, cover-up, grounds — right ratings, inspected, in test date
■ Check the weather: wind, lightning, heat, ice — conditions that stop or change the job
■ Identify the access, the work zone, traffic control, and the public exposure
■ Know the location: address, nearest cross-streets, gate codes — for emergency response
■ Plan the rescue BEFORE the work — not after the incident
Module 5 — In the Field
Powerline Electrical Theory & Safety | 80

## Slide 81
5.2 HAZARD ASSESSMENT
Hazard Assessment / Job Safety Analysis (JSA)
■ Break the job into steps; for each step identify the hazards and the controls
■ Electrical hazards: energized parts, second points of contact, induced voltage, fault energy
■ Mechanical/physical: falls, dropped objects, pinch points, equipment, rigging, tension
■ Environmental: weather, traffic, terrain, wildlife, confined/excavation, public
■ For each hazard, select the control from the hierarchy — eliminate where you can
■ Reassess when ANYTHING changes: scope, weather, crew, equipment, the unexpected
KEY CONCEPT
The four questions
– What am I about to do? What can hurt me?
– How do I control it? What if the plan changes?
– A JSA is a living document — update it as the job evolves.
Module 5 — In the Field
Powerline Electrical Theory & Safety | 81

## Slide 82
5.3 TAILBOARD
The Tailboard / Job Briefing — What & Why
The tailboard is where the plan in your head becomes the plan in everyone's head.
■ A tailboard is the crew safety briefing held before work starts (and again when things change)
■ Required before each job; it aligns the whole crew on the plan and the hazards
■ OSHA 1910.269(c) requires a job briefing covering at minimum:
  – Hazards associated with the job
  – Work procedures involved
  – Special precautions
  – Energy-source controls (clearances, grounds, LOTO)
  – Personal protective equipment requirements
■ More extensive briefing for complex/hazardous jobs; brief again after interruptions or changes
Module 5 — In the Field
Powerline Electrical Theory & Safety | 82

## Slide 83
5.3 BRIEFING
Running an Effective Tailboard
1
1. Describe the job
What are we doing, where, on what equipment, energized or de-energized, at what voltage.
2
2. Walk the hazards
Go through the JSA: electrical (second points, MAD, induction), falls, traffic, weather, public.
3
3. State the controls
Cover-up plan, grounds/EPZ, LOTO/clearance, MAD, PPE, traffic control — specific, not generic.
4
4. Assign roles
Person in charge, who works, who tends, who grounds, who watches, who calls for help.
5
5. Confirm rescue & comms
Location/address, nearest hospital, rescue plan & equipment, radio/phone, hand signals.
6
6. Engage the crew
Ask questions, invite input, confirm understanding — everyone has stop-work authority.
Module 5 — In the Field
Powerline Electrical Theory & Safety | 83

## Slide 84
5.4 ROLES
Roles & Responsibilities on the Crew
Key roles
■ Person-in-Charge / Crew Leader — owns the plan & clearance
■ Qualified worker(s) — perform the energized/skilled tasks
■ Groundman / tender — supports, tends ropes, handles materials
■ Safety watch / second person — eyes on the worker, ready to act
■ Flagger / traffic control — protects the work zone & public
Shared responsibilities
■ Everyone: know the plan and your part in it
■ Everyone: maintain situational awareness
■ Everyone has STOP-WORK authority — use it without fear
■ Speak up: a question now beats an incident later
■ No solo energized work — a qualified second person is present
Module 5 — In the Field
Powerline Electrical Theory & Safety | 84

## Slide 85
5.5 COMMUNICATION
Communication — The Glue That Holds the Job Together
■ Use clear, standardized language for switching and clearances — no ambiguity
■ Three-way communication for critical commands: state → repeat back → confirm
■ Confirm clearances and grounds with the system operator before and after
■ Agree on hand signals for crane/bucket/rigging where radios are hard to hear
■ Announce movements: 'coming down', 'tension on', 'clear' — keep the crew in the loop
■ Re-brief after ANY interruption, crew change, or scope change
■ If you're not sure what was said, STOP and confirm — assumptions kill
Module 5 — In the Field
Powerline Electrical Theory & Safety | 85

## Slide 86
5.6 RESCUE
Emergency Response & Rescue — Plan It Before You Need It
■ Every energized/elevated job needs a rescue plan briefed in the tailboard
■ Pole-top & bucket rescue: trained crew can lower an injured worker quickly
  – Know the equipment (handline, rescue device) and practice the procedure
■ Do NOT become the second victim — ensure the source of contact is removed/de-energized first
■ Call for help early: know the address, cross-streets, and access
■ CPR + AED for electrical contact / cardiac arrest — minutes matter; know where the AED is
■ After contact, ALWAYS transport for medical evaluation — internal injury can be hidden
WARNING ⚠
The first rule of rescue
– Protect yourself first — a rescuer who gets electrocuted helps no one.
– De-energize / remove the source, then reach the patient.
– Speed saves lives, but only a SAFE rescue saves two.
Module 5 — In the Field
Powerline Electrical Theory & Safety | 86

## Slide 87
5.7 ENVIRONMENT
Weather, Environment & Public Safety
■ Lightning / approaching storms: stop work and clear elevated/exposed positions
■ High wind: affects conductors, booms, rigging, and footing — know your limits
■ Wet conditions: drastically reduce body & equipment insulation — reassess hot work
■ Heat/cold: fatigue and impaired judgment are hazards in themselves — hydrate, rotate
■ Ice/snow loading: added conductor weight and slip hazards
■ Public protection: barricades, signage, traffic control; keep bystanders clear of downed lines
■ Wildlife & vegetation: animals cause faults; trees create clearance & contact hazards
Module 5 — In the Field
Powerline Electrical Theory & Safety | 87

## Slide 88
ILLUSTRATED
The Tailboard Briefing
The crew briefing aligns everyone: hazards, procedures, controls, PPE, roles, and rescue.
Module 5 — In the Field
Powerline Electrical Theory & Safety | 88

## Slide 89
ILLUSTRATED
Switching & the Clearance
A clearance isolates the work zone: open, locked, tagged, tested dead, and grounded on every side.
Module 5 — In the Field
Powerline Electrical Theory & Safety | 89

## Slide 90
ILLUSTRATED
Pole-Top Rescue
Remove the source first, lower the patient, start CPR & AED — never become the second victim.
Module 5 — In the Field
Powerline Electrical Theory & Safety | 90

## Slide 91
MODULE 5 RECAP
Module 5 — Key Takeaways
■ Plan the job — and the rescue — before boots leave the truck
■ A JSA pairs every step with its hazards and controls, and updates when things change
■ The tailboard puts the plan in everyone's head: hazards, procedures, controls, PPE, roles
■ Define roles and use disciplined, three-way communication
■ Everyone has stop-work authority — and the obligation to use it
■ Rescue first protects the rescuer; after any contact, get medical evaluation
Module 5 — In the Field
Powerline Electrical Theory & Safety | 91

## Slide 92
MODULE
6
Regulations & Standards
— OSHA 1910.269 & 1926 Subpart V
— The National Electrical Safety Code (NESC)
— ASTM & IEEE equipment standards
— Qualification & apprenticeship
— Recordkeeping & program duties

## Slide 93
6.1 WHY REGS
Why Regulations Exist — and Why You Should Know Them
■ Every safe-work rule in this course is backed by a regulation or consensus standard
■ Regulations set the MINIMUM — your employer's program may be stricter (follow the stricter)
■ Knowing the 'why' and the 'where it's written' makes you a better, safer, more credible worker
■ The big three for line work:
  – OSHA — federal law: how the work must be done safely (enforceable)
  – NESC (IEEE C2) — how the system is built, spaced, and maintained
  – ASTM / IEEE / ANSI — how the tools and PPE are made, rated, and tested
■ Compliance is the floor; the goal is everyone home safe — which often means going beyond the floor
Module 6 — Regulations & Standards
Powerline Electrical Theory & Safety | 93

## Slide 94
6.2 OSHA 1910.269
OSHA 1910.269 — Electric Power Generation, Transmission & Distribution
If you read one regulation cover to cover, make it this one.
■ The primary OSHA standard for operating & maintaining electric power systems (general industry)
■ Key provisions every lineworker should know:
  – (a) Training & qualified-employee requirements
  – (c) Job briefings (the tailboard) — required content and frequency
  – (l) Working on or near energized parts; minimum approach distances (Tables R-3 / R-6)
  – (m) De-energizing lines & equipment
  – (n) Grounding for the protection of employees
  – Arc-flash hazard assessment and arc-rated apparel requirements
■ Companion construction standard: 29 CFR 1926 Subpart V (power transmission & distribution)
Module 6 — Regulations & Standards
Powerline Electrical Theory & Safety | 94

## Slide 95
6.2 SCOPE
OSHA 1910.269 vs 1926 Subpart V
1910.269 (General Industry)
■ Operation & MAINTENANCE of existing power systems
■ Day-to-day line & substation work
■ Job briefings, MAD, de-energizing, grounding
■ Harmonized with Subpart V on key requirements
1926 Subpart V (Construction)
■ CONSTRUCTION of power transmission & distribution
■ Building new lines and major rebuilds
■ Mirrors 1910.269 on MAD, briefings, grounding
■ Use the standard that matches the type of work
Module 6 — Regulations & Standards
Powerline Electrical Theory & Safety | 95

## Slide 96
6.3 NESC
The National Electrical Safety Code (NESC / IEEE C2)
■ NESC governs the safe installation, operation & maintenance of utility electric & communication systems
■ Distinct from the NEC (NFPA 70), which covers premises/building wiring
■ Sets rules for the SYSTEM that protect both workers and the public, including:
  – Conductor clearances — ground, structures, other lines, and to the public
  – Strength & loading of structures; grades of construction
  – Grounding methods and worker safety rules (Part 4 covers work rules)
■ Updated on a multi-year cycle; the edition in force depends on jurisdiction
■ When clearances or construction look wrong in the field — NESC is the reference
Module 6 — Regulations & Standards
Powerline Electrical Theory & Safety | 96

## Slide 97
6.4 ASTM/IEEE
Key ASTM / IEEE / ANSI Equipment Standards
Standard | Covers
ASTM D120 | Rubber insulating GLOVES — manufacture & rating
ASTM D1051 | Rubber insulating SLEEVES
ASTM D1048 | Rubber insulating BLANKETS
ASTM D1049 / D1050 | Insulating COVERS / LINE HOSE
ASTM F496 | In-service CARE of rubber gloves & sleeves (test intervals)
ASTM F478 | In-service care of insulating LINE HOSE & covers
ASTM F711 | Fiberglass rod & tube for LIVE-LINE TOOLS
ASTM F855 | Temporary protective GROUNDS (clamps & cables)
ASTM F1506 / NFPA 70E | Arc-rated FR CLOTHING & arc-flash protection
IEEE C2 (NESC) | Utility system safety code
ANSI Z89.1 | Hard hats (electrical Class E)
These standards define how your PPE and tools are built, rated, and re-tested — the numbers on your gloves and grounds trace back here.
Module 6 — Regulations & Standards
Powerline Electrical Theory & Safety | 97

## Slide 98
6.5 QUALIFICATION
Qualified Workers, Training & Apprenticeship
■ OSHA requires that only QUALIFIED employees work on or near energized parts
■ Qualified = trained AND able to demonstrate skills/knowledge for the construction & operation involved
  – Knows how to distinguish energized parts, determine voltages, and maintain MAD
■ Lineworker apprenticeships (often ~3–4 years, thousands of OJT hours) build that qualification
  – Classroom theory + supervised on-the-job training + skills verification
■ Ongoing training: refreshers, new procedures, CPR/AED & pole-top rescue, equipment-specific
■ Document training and re-qualification — it is both a legal requirement and proof of competence
Module 6 — Regulations & Standards
Powerline Electrical Theory & Safety | 98

## Slide 99
6.6 RECORDS
Recordkeeping & Program Responsibilities
Records to keep
■ Training & qualification records
■ PPE/tool inspection & electrical test dates
■ Job briefings / tailboards (per program)
■ Switching orders, clearances & grounding records
■ Incident & near-miss reports and investigations
Employer program duties
■ Written safe-work & electrical safety program
■ Hazard/arc-flash assessments & MAD tables
■ Provide & maintain rated PPE and tools
■ Enforce procedures; support stop-work authority
■ Investigate, learn, and improve after every event
Module 6 — Regulations & Standards
Powerline Electrical Theory & Safety | 99

## Slide 100
MODULE 6 RECAP
Module 6 — Key Takeaways
■ Regulations set the minimum; your program may be stricter — always follow the stricter rule
■ OSHA 1910.269 (and 1926 Subpart V) govern how the work is done — briefings, MAD, LOTO, grounding
■ NESC (IEEE C2) governs how the system is built, spaced, and maintained
■ ASTM/IEEE/ANSI define how your PPE & tools are rated and tested
■ Only qualified workers do energized work — earned through apprenticeship & ongoing training
■ Keep records: training, test dates, briefings, clearances, incidents
Module 6 — Regulations & Standards
Powerline Electrical Theory & Safety | 100

## Slide 101
MODULE
✓
Bringing It All Together
— The mental model from theory to the field
— Daily safe-work disciplines
— Final reminders
— Resources & references

## Slide 102
SYNTHESIS
From Theory to the Field — The Mental Model
1
Understand the energy
Voltage pushes current; current through you kills. Know your voltage class and fault energy.
2
Find the circuit
Where would current flow through ME? Locate the SECOND POINT OF CONTACT — every time.
3
Choose the control
De-energize if you can. If hot: isolate AND insulate — MAD, cover-up, gloves, grounds, EPZ.
4
Verify
Test the tester, test-before-touch, prove dead, apply grounds, inspect every piece of PPE.
5
Brief & assign
Tailboard the hazards, controls, roles, comms, and rescue. Everyone understands. Everyone can stop work.
6
Work & reassess
Maintain controls all the way through. When ANYTHING changes — stop, re-brief, re-assess.
Course Wrap-Up
Powerline Electrical Theory & Safety | 102

## Slide 103
DAILY DISCIPLINE
Ten Disciplines That Keep Crews Alive
If you remember nothing else, remember these.
■ Treat every conductor as energized until YOU prove it dead and grounded
■ Always identify and eliminate the second point of contact
■ Maintain minimum approach distance — for your body, tools, and equipment
■ Cover up: nearest hazard first, remove in reverse
■ Test the tester before and after; test-before-touch
■ Ground and bond an equipotential zone at the work site
■ Inspect rubber goods and tools before every use; honor test dates
■ Hold a real tailboard — and re-brief when anything changes
■ Plan the rescue before the work; never become the second victim
■ Use your stop-work authority — no job is worth your life
Course Wrap-Up
Powerline Electrical Theory & Safety | 103

## Slide 104
CLOSING
Final Word
■ Electricity is invisible, silent, and unforgiving — but it is also entirely predictable
■ It follows the same laws every time, which means the hazard is always controllable
■ The theory in Module 1 is not academic — it is WHY every rule in Modules 3–6 works
■ Skills fade and complacency creeps in — that is why we train, brief, and reassess relentlessly
■ Look out for the worker next to you as carefully as you look out for yourself
BEST PRACTICE
The whole point
– Everyone goes home, every day.
– That is the only acceptable outcome of any job — and it is achievable on every job.
Course Wrap-Up
Powerline Electrical Theory & Safety | 104

## Slide 105
REFERENCES
Resources & References
Regulations & codes
■ OSHA 29 CFR 1910.269 — GT&D (general industry)
■ OSHA 29 CFR 1926 Subpart V — construction
■ OSHA 1910.137 — electrical protective equipment
■ OSHA 1910.147 — control of hazardous energy (LOTO)
■ NESC — IEEE C2; NFPA 70E — arc-flash safety
Standards & training
■ ASTM F18 committee standards (D120, F496, F855, etc.)
■ IEEE standards for live-line work & grounding
■ Your employer's safe-work practices & MAD tables
■ Apprenticeship program materials & manufacturer manuals
■ First aid / CPR / AED & pole-top rescue certification
Course Wrap-Up
Powerline Electrical Theory & Safety | 105

## Slide 106
Questions & Discussion
Review the hazards on YOUR system, with YOUR equipment, against YOUR procedures.
Stay sharp. Watch your second point of contact. Everyone goes home.